## Brochure Data
Category | Parameter | Value | Unit | PDF page | Status | Note
Plant | Installed capacity | 1450 | MW | 4 | Brochure | 5 x 290 MW (p.4, p.17)
Plant | Average annual energy | 6600 | GWh | 4 | Brochure
Plant | Number of units | 5 | - | 12 | Brochure
Plant | Rated output per unit | 290 | MW | 17 | Brochure | pp.4, 7, 17
Plant | Turbine full-gate output | 295 | MW | 12 | Brochure - conflict | Differs from 290 MW; assumed full-gate maximum (assumption)
Plant | Gross river drop (Tarbela tailrace to Haro confluence) | 76 | m | 4 | Brochure | Over 63 km reach
Plant | Reach length for river drop | 63 | km | 4 | Brochure
Plant | Design head | 69 | m | 17 | Brochure
Plant | Combined generating efficiency | 94 | % | 17 | Brochure | Five Francis turbines + generators
Plant | Design flow per unit, optimum gate | 400 | m3/s | 17 | Brochure
Plant | Design flow per unit, full gate | 460 | m3/s | 17 | Brochure | p.7 and p.17
Plant | Turbine type | Francis | - | 12 | Brochure
Plant | Peak generation duration supported | 4 | h | 7 | Brochure | Headpond live storage supports ~4 h daily peak
Electrical | Transformer rating (single-phase unit) | 107.5 | MVA | 17 | Brochure | p.12 lists 3 x 107.5 MVA per bank
Electrical | Transformer banks (3-phase) | 5 | - | 17 | Brochure
Electrical | Rated voltage HV:LV | 515v 3:18 | kV | 12 | Brochure - ambiguous | Garbled in source; probably 500/sqrt(3) : 18 kV, unconfirmed
Electrical | Switchyard 500 kV bays | 6 | - | 12 | Brochure
Electrical | Switchyard layout | Breaker and half | - | 12 | Brochure
Electrical | Transmission | 500 kV double circuit | kV | 17 | Brochure | To WAPDA national grid
Electrical | Cranes (count) | 12 | - | 17 | Brochure | Capacity 6 to 450 t
Electrical | Control system | 2 DCS (Barrage, Power Complex), fibre-optic link | - | 17 | Brochure
Penstock | Number | 5 | - | 12 | Brochure
Penstock | Diameter | 10.6 | m | 12 | Brochure
Penstock | Length | 222 | m | 12 | Brochure
Barrage | Normal pond level | 340 | m | 12 | Brochure
Barrage | Design flood | 18700 | m3/s | 12 | Brochure
Barrage | Survival flood | 46200 | m3/s | 12 | Brochure
Barrage | Standard bays - openings | 20 | - | 12 | Brochure
Barrage | Standard bays - crest level | 332.2 | m | 12 | Brochure
Barrage | Head regulator - openings | 8 | - | 12 | Brochure
Barrage | Head regulator - crest level | 333 | m | 12 | Brochure
Barrage | Undersluices - openings | 8 | - | 12 | Brochure
Barrage | Undersluices - crest level | 326 | m | 12 | Brochure
Power channel | Design flow | 1600 | m3/s | 12 | Brochure
Power channel | Length | 51906 | m | 12 | Brochure
Power channel | Longitudinal slope | 1:9600 | - | 12 | Brochure
Power channel | Full supply depth | 9 | m | 12 | Brochure
Power channel | Bed width | 58.4 | m | 12 | Brochure
Power channel | Side slope | 1V:2H | - | 12 | Brochure
Power channel | Lining thickness | 135 | mm | 12 | Brochure
Power channel | Road bridges | 34 | - | 12 | Brochure
Power channel | Railway bridge | 1 | - | 12 | Brochure
Power channel | Pedestrian crossings | 12 | - | 12 | Brochure
Power channel | Superpassages | 27 | - | 12 | Brochure
Power channel | Drainage inlets | 24 | - | 12 | Brochure
Power channel | Escapes | 5 | - | 12 | Brochure
Power channel | Culverts | 1 | - | 12 | Brochure
Power complex | Headponds normal pond level | 334 | m | 12 | Brochure
Power complex | Headponds live volume (two ponds combined) | 25.5 | Mm3 | 12 | Brochure | p.7: approx. 25.5 million m3
Power complex | Siphon spillway discharge capacity | 1600 | m3/s | 12 | Brochure
Power complex | Siphon spillway crest level | 334.5 | m | 12 | Brochure
Power complex | Intake - openings | 10 | - | 12 | Brochure
Power complex | Intake - crest level | 305.5 | m | 12 | Brochure
Power complex | South sill - openings | 3 | - | 12 | Brochure
Power complex | South sill - level | 323 | m | 12 | Brochure
Power complex | North sill - openings | 10 | - | 12 | Brochure
Power complex | North sill - level | 321 | m | 12 | Brochure
Project | Cost approved (PC-I, July 1994) | 89840 | million Rs | 13 | Brochure
Project | Actual cost incurred | 96957 | million Rs | 13 | Brochure
Project | EIRR | 22.19 | % | 13 | Brochure
Project | FIRR | 13.76 | % | 13 | Brochure
Project | Units 1-2 commissioned | 19 Aug 2003 | - | 15 | Brochure
Project | Unit 5 commissioned | Apr 2004 | - | 13 | Brochure
Project | North headpond completed | Dec 2004 | - | 13 | Brochure
Legend: blue = value from brochure (editable); yellow rows = conflict/ambiguity. PDF page = page index in the attached file. p.5 duplicates p.4.

## Missing Data
Group | Missing parameter | Not in brochure | Planned handling
Generator | Rated MVA and power factor | Yes | Typical textbook value, tagged Assumption, user-overwritable
Generator | Rated voltage (brochure value unconfirmed) | Yes | Typical textbook value, tagged Assumption, user-overwritable
Generator | Speed / number of poles | Yes | Typical textbook value, tagged Assumption, user-overwritable
Generator | System frequency (50 Hz expected, not stated) | Yes | Typical textbook value, tagged Assumption, user-overwritable
Generator | Inertia constant H | Yes | Typical textbook value, tagged Assumption, user-overwritable
Generator | Reactances and time constants | Yes | Typical textbook value, tagged Assumption, user-overwritable
Generator | Excitation system data | Yes | Typical textbook value, tagged Assumption, user-overwritable
Turbine/governor | Rated speed | Yes | Typical textbook value, tagged Assumption, user-overwritable
Turbine/governor | Runner diameter | Yes | Typical textbook value, tagged Assumption, user-overwritable
Turbine/governor | Efficiency curve | Yes | Typical textbook value, tagged Assumption, user-overwritable
Turbine/governor | Gate servo and governor parameters | Yes | Typical textbook value, tagged Assumption, user-overwritable
Turbine/governor | Water starting time | Yes | Typical textbook value, tagged Assumption, user-overwritable
Hydraulics | Headpond surface area and level-volume curve | Yes | Typical textbook value, tagged Assumption, user-overwritable
Hydraulics | Minimum operating level | Yes | Typical textbook value, tagged Assumption, user-overwritable
Hydraulics | Tailwater rating curve | Yes | Typical textbook value, tagged Assumption, user-overwritable
Hydraulics | Penstock losses and wave speed | Yes | Typical textbook value, tagged Assumption, user-overwritable
Hydraulics | Channel roughness | Yes | Typical textbook value, tagged Assumption, user-overwritable
Hydraulics | Tarbela release profile | Yes | Typical textbook value, tagged Assumption, user-overwritable
Grid/transformer | Transformer impedance | Yes | Typical textbook value, tagged Assumption, user-overwritable
Grid/transformer | Tap ratio | Yes | Typical textbook value, tagged Assumption, user-overwritable
Grid/transformer | Grid short-circuit level | Yes | Typical textbook value, tagged Assumption, user-overwritable
Grid/transformer | Load profile | Yes | Typical textbook value, tagged Assumption, user-overwritable

## Plan
Phase | Deliverable | Contents | Test before moving on
0 | Data file | data/brochure.json (each value tagged brochure/assumption + page), assumptions.md, PROGRESS.md | Values match Brochure Data sheet
1 | Python state-space model, one unit | Headpond level, penstock flow (rigid column), gate servo, rotor speed/angle; linearise to A,B,C,D | Steady state P = rho g Q H eta approx 293 MW; eigenvalues stable; step responses plausible
2 | JS simulation engine | RK4, 1-5 units switchable, PI governor | Matches Python results within tolerance
3 | Dashboard | MW, flow, pond level, speed, unit on/off, load-step controls | Run scenarios, compare with Phase 1
4 | Three.js 3D scene | Primitives sized from brochure data: barrage, channel (schematic scale), headponds, penstocks, powerhouse; driven by sim | Visual check; sim-to-scene binding works
5 | Integration and report | Validation notes, short report | Full run-through

## Sanity Check
Item | Value | Unit | Basis
Water density | 1000 | kg/m3 | Assumption (standard value)
Gravity | 9.81 | m/s2 | Assumption (standard value)
Flow per unit, full gate | 460 | m3/s | Brochure
Design head | 69 | m | Brochure
Efficiency | 0.94 | fraction | Brochure
Computed electrical output per unit | 292.6872 | MW | Simulated: P = rho g Q H eta
Brochure rated output per unit | 290 | MW | Brochure
Brochure full-gate output | 295 | MW | Brochure
Difference vs rated | 2.6872 | MW | Calculated
Difference vs full-gate | -2.3128 | MW | Calculated
Total plant (5 units, computed) | 1463.4362 | MW | Simulated